## Slide 1
DOE/NETL Project Closeout Meeting
Pittsburgh, PA / June 14, 2022
Full-Scale FEED Study For a 816 MWe Capture Plant at the Prairie State Generating Company Using Mitsubishi Heavy Industries of America Technology
Kevin C OBrien, PhD Director, Illinois Sustainable Technology Center Director, Illinois State Water Survey Prairie Research Institute University of Illinois at Urbana-Champaign

## Slide 2
Disclaimer
This report was prepared as an account of work sponsored by an agency of the United States Government. Neither the United States Government nor any agency thereof, nor any of their employees, makes any warranty, express or implied, or assumes any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, apparatus, product, or process disclosed, or represents that its use would not infringe privately owned rights. Reference herein to any specific commercial product, process, or service by trade name, trademark, manufacturer, or otherwise does not necessarily constitute or imply its endorsement, recommendation, or favoring by the United States Government or any agency thereof. The views and opinions of authors expressed herein do not necessarily state or reflect those of the United States Government or any agency thereof.

## Slide 3: Agenda
Introduction, Overview & Summary of Results (UIUC)
Results of Studies and Investigations
  UIUC Lead Investigations (UIUC)
  S&L/Kiewit Lead Investigations (Kiewit)
  MHI Lead Investigations (MHI)
  Constructability Review (Kiewit)
  Outline of Resulting Plot Plan (Kiewit)
ISBL Detailed Design Results (MHI)
OSBL Detailed Design Results (Kiewit)
Overall Plant Performance (Kiewit)
Overall Plant Cost (Kiewit)
Closing Discussions (PSGC)

## Slide 4: PROJECT OBJECTIVES: Overall: Perform a Front-End Engineering Design (FEED) study for the retrofit of the Prairie State Generation Company’s (PSGC) coal-fired power plant with post-combustion carbon capture. The FEED study will outline the use of Mitsubishi Heavy Industries’ (MHI) Advanced KM CDR Process™ to retrofit one of PSGC’s two generating units (approximately 816 MWe). The FEED study will enable PSGC to move forward with actual build/operate in future work.
Cooperative Agreement No. DE-FE0031841
PROJECT OVERVIEW
Funding: $17,509,676 DOE: $14,004,676 20% Cost Share: $3,505,000 (PSGC)
Work Period: 1 Jan 2020 – 31 Dec 2021
Incurred Expenses (1 April 2022)
DOE: $13,349,525
Cost Share: $3,454,337

## Slide 5: Project Team Management Structure

## Slide 6: THE TECHNOLOGY
FRONT-END ENGINEERING DESIGN STUDIES FOR CARBON CAPTURE SYSTEMS ON COAL AND NATURAL GAS POWER PLANTS

## Slide 7: Mitsubishi Heavy Industries’ (MHI) Advanced KM CDR Process™

## Slide 8: KS-21TM Solvent
MHI has been able to conclude that there are likely operating cost benefits for using KS-21™ instead of KS-1™
KS-21™ has several advantageous properties such as lower volatility and greater stability which result in:
  Lower amine emissions
  Lower solvent make-up
  Lower compression energy

## Slide 9: THE PROJECT
FRONT-END ENGINEERING DESIGN STUDIES FOR CARBON CAPTURE SYSTEMS ON COAL AND NATURAL GAS POWER PLANTS

## Slide 10: Project Tasks
Task # | Task
1.0 | Project Management and Planning
2.0 | Front-End Engineering Design (FEED) Study
2.1 | Design Basis
2.2 | Preliminary Engineering
2.3 | ISBL Detailed Engineering
2.4 | OSBL Detailed Engineering
2.5 | Studies and Investigations
2.6 | Cost Assessment
3.0 | Regulatory and Permitting at Host Site
4.0 | Final FEED Study Package

## Slide 11: Project Milestones
Task # | Deliverable Title | Due Date
1.0 | Project Management Plan Update | 3/3/2020
2.0 | Design Basis Document Complete | 10/30/20
2.0 | Report on Utility Requirements | 11/19/20
3.0 | Preliminary Regulatory and Permitting Pathway | 2/18/21
2.0 | HAZOP Review | 4/30/21
2.0 | Impact on Kaskaskia Watershed Document Complete | 5/28/21
2.0 | Constructability Review Complete | 6/30/21
3.0 | Regulatory and Permitting Analysis Complete | 8/6/2021
2.0 | Detailed Engineering Document Complete | 11/30/21
4.0 | Final Report Submitted | 12/31/21
4.0 | FEED Study Package Complete | 12/31/21
All quarterly advisory board meetings were held as planned

## Slide 12: Project Timeline
Project was completed within budget and on-time despite challenges due to COVID-19 pandemic

## Slide 13: Summary of Results
8,462,000 ston annually of CO2
Project Capital Cost Estimate (+/- 15%)
  $2,044,465,000
Cost of Capture
  $43.42/metric tonne of CO2

## Slide 14: Studies and Investigations
UIUC Lead Studies
    Water Supply Study
    Air Permitting Pathway
    Water Permitting Pathway

## Slide 15: Water Supply Study
Draw raw water from the Kaskaskia River
  14 million gallons per day (mgd)
Build a storage pond for drought conditions
  Water is available for use during wet (normal) conditions
  No allocation remaining, unable to draw water during drought conditions
  Store 26 days of water (25-year drought)

## Slide 16: Regulatory and Permitting at Host Site
Air Permitting Pathway
Carbon Capture Plant as a Separate Source with Only Emissions Created by the Carbon Capture Plant Subject to Permitting
Advantages
Carbon capture plant will have own air permit with no overlapping requirements
Only address emissions generated by carbon capture plant
Disadvantages
IEPA may impose new requirements to PSGC existing permits
  Believed to be unlikely given that the monitoring of emission could be implemented upstream of the divergence of the flue gas to the carbon capture plant

## Slide 17
Water Permitting Pathway
Raw Makeup Water
File a request to Illinois Department of Natural Resources (IDNR) to use public water from the Kaskaskia River
  New construction activities outside waterway - only a request to use public water is needed to be filed to IDNR.
  New construction activities inside waterway - a joint permit application to IDNR, Illinois Environmental Protection Agency (IEPA), and USACE will be required
Limiting conditions based on draw needs during draught conditions
  May be able to gain allocation rights if other users shutdown operations
Regulatory and Permitting cont.

## Slide 18
Water Permitting Pathway
Wastewater
Discharging treated cooling tower blowdown into the Kaskaskia River will require a National Pollutant Discharge Elimination System (NPDES) permit
Removal of trace metals to the concentrations indicated in 35 Illinois Administrative Code (IAC) 302
  No mixing zone at the new cooling tower blowdown discharge to the Kaskaskia River will be allowed.
NPDES discharge limitations for total suspended solids (TSS) expected to be like existing PSGC cooling tower blowdown
Regulatory and Permitting cont.

## Slide 19: Studies and Investigations
Kiewit and S&L Lead Studies
    Site Selection
    Ammonia Scrubber Study
    Cooling Sourcing Study
    Water and Wastewater Treatment Study
    Steam and Electric Sourcing Study
    Flue Gas Tie-In Study

## Slide 20: Site Selection
West
Rail Loop
East
North
North
West
Rail
East
Notes: Show all option that were considered and inside rail loop and East were narrowed down for final consideration.
Reason for elimination to be discussed later.

## Slide 21
West
Rail Loop
East
North
West and North Locations​
Ruled out after consulting with Mine Engineer
Concerns of causing structural issues
Use of either site would require extensive mine remediation​
Site Selection
Rail Loop
  Tight location, Requires Modifications to Rail Loop, Prevents future power block use of this area
  Shortest Duct Length
  Extended Impact to Power Plant Operations during construction
East Location SELECTED
  Requires longer Ducting – optimized with diagonal path
  More land availability
  Clean separation of company assets with physical barriers
Notes: Show all option that were considered and inside rail loop and East were narrowed down for final consideration.
Reason for elimination to be discussed later.

## Slide 22
Evaluated: Ammonia Scrubber and separate Quencher
  Additional material handling system required to produce Ammonia sulfate
Ammonia Scrubber Study
Notes: Integrated scrubber / quencher not feasible
MET would need to study effect combining an ammonia scrubber with quencher might have on the byproduct quality - critical to having a salable output.
Marsulex Environmental Technologies (MET) was contacted to provide a budgetary quote and info on their ammonia scrubber.

## Slide 23: Ammonia Scrubber Study
Results:
  Table Below
  Payback Period >25 years
Conclusion:
  Insufficient economic benefit to justify added complexity
  Integrated Quencher (Base) Selected
 | Base | Ammonia Scrubber
Capital Cost | Base | 103,954,000
First Year Operating Costs, $/yr | 2,780,000 | (5,958,000)

## Slide 24: Cooling Sourcing Study
Evaluated best-fit cooling technology for project
Evaluated Technologies
  Mechanical Draft Cooling Tower(MDCT)
  Hybrid MDCT/Air-Cooled Fin Fan Heat Exchanger(FFHE)
  Wet Surface Air Cooler(WSAC)
Description | Cost | Recommended | Notes
MDCT | $14MM | Yes | Lowest Cost.
Hybrid MDCT/FFHE | - | No | Not technically feasible. Hot water temperature is low relative to high ambient, no benefit.
WSAC | $36MM | No | High cost. 50% water savings.
Notes: MDCT we also considered shapes for the Mechanical draft towers. The Octaonal tower shape results in less downsdraft during high winds and much higher plume b

## Slide 25
Evaluation of available treatment options, maximize re-use, and minimize overall cost.
Water Sources:
  Kaskaskia River
  Quencher Blowdown
Requirements Driving Water Treatment Equipment:
  Cooling Tower Makeup
  Steam Generation System Makeup
  Carbon Capture system Makeup
  NPDES Permit Discharge Requirements
Illinois Administrative Code(IAC)
IAC 302 limits indicative of the most
stringent limits that may be applied.
Determined to be appropriate
for this study.
Water and Wastewater Treatment

## Slide 26
Results:
Water Sources:
  Water Inputs:
    8,300 gpm makeup water required from Kakaskia River
    2,300 gpm Caustic Flue Gas Condensate Wastewater
  Discharge:
    3,450 gpm to New Kakaskia River Outfall
Treatment Selected:
  Raw Water Treatment(CT Makeup): Hardness and TSS removal by lime softening, clarification, and multi-media filtration
  Demineralized Water(Steam and CC Makeup): TDS Removal by RO
  Wastewater Treatment: Trace Metal Removal by sulfide precipitation
Water and Wastewater Treatment
Notes: Room for some slight increase to COC, reducing blowdown and makeup water required.
8000 gpm is roughly equal to the makeup water consumed by unit 2.

## Slide 27
Steam and Electric Sourcing Study
Evaluation of available options for providing the facility with steam and electricity.
Option 1: Package boilers, power from grid
Option 2: Co-generation facility employing gas-fired CTs
Option 3: Co-generation with package boilers and a backpressure steam turbine for power generation.
Option 2 was broken down into four sub-options:
Option 2a – 1x SGT6-800 CT, package boilers
Option 2b – 1x SGT6-2000E CT + HRSG, package boilers
Option 2c – 2xGE7F.04 CTs + HRSGs, package boiler
Option 2d – 3x3 Combined Cycle SGT6-2000E CTs
Steam integration with host plant was initially explored, but this option was eliminated from further evaluation as host plant could not accept a derate.
Notes: Worth noting why we use 8 package boilers instead of 1 combined boiler. It’s cheaper.

## Slide 28
Steam and Electric Sourcing Study
Option 2, Challenges with Co-generation Configurations
  Power generated and steam output do not align well with capture facility needs. All configurations require one or both of (a) auxiliary boilers to supplement steam (b) sale of excess power to market.
  PSGC did not want to generate significant additional power that would need to be sold
  The large quantity of low-quality steam, as required for the capture plant, would require a specialized HRSG design which would need to be developed.
Results below:
Option 1 Selected, Lowest Cost
*Evaluated Cost and Cost of Capture do not include ISBL costs.
Option | Description: | Notes: | Evaluated Cost* | Evaluated Cost of Capture* | Selected
1 | Package Boilers | Lowest CAPEX | $496MM | $23.91 | X
3 | Package Boilers with BP Steam Turbine | Higher Capex, Lowest Cost of Capture | $570MM ($74MM) | $23.59 $0.32 | 
Notes: All options would require
NG pipeline
Switchyard upgrades (either to bring in power or to export excess power)
Added costs with BPST included
1) Large boilers to produce higher pressure steam
2) Alloy piping required for higher pressure steam(between boiler and STG)
3) LPS piping
4) Added equipment (STG)
BPST reduces risk of exposure

## Slide 29: Flue Gas Tie-In Study
Purpose:
Calculate pressure drop for use sizing MHI flue gas fans
Provide preliminary tie-in/duct design
Identify opportunities and risks for further investigation
Stack
New Duct
To Capture
Existing
Wet ESP
Outlet
Plenum
Tie-In Location
Notes: Tie-In Location is downstream of existing Wet Electrostatic Precipitator (WESP) and upstream of existing stack.
Damper locations, and the control interface between the existing plant and carbon capture were an area of discussion.

## Slide 30: Flue Gas Tie-In Study
Pressure Drop Results
  Train 1&3: 9.05 inWC
  Train 2&4: 8.04 inWC
  From Wet ESP inlet to Quencher Inlet (ISBL Scope)
Flow Modifications to Existing Wet ESP Outlet Plenum(right)
Opportunities
  Optimization of Vane Placement
Risk Mitigation, Example
  Mixing at Quencher Inlet; control instrumentation
  Allowance for study during project
  Agreed Plan to reconfigure instrumentation if proper mixing cannot be achieved
Notes: From study:
Note that these results are indicative of design that has not been optimized with flow correction devices; in certain
areas where there is high turbulence impacting the convergence of the model, vanes were added. Vanes have not been
optimized for pressure drop or flow mixing; instead they have been placed to minimally help with pressure drop while
trying to minimize the effect on the flow to the existing stack

## Slide 31: Studies and Investigations
MHI Studies
    Flue Gas Testing
    Transportation Study
    Hazard and Operability (HAZOP) Review

## Slide 33
•Inland Transportation Studies Made
•Module Size decided
•Challenges
Need to modify Power(44)/Utility Lines prior to the Module transportation which will take 9 months Engineering and 18 months modification work
Dock | Location | Distance to Site | Selected
Ingram Dock | Mississippi River | 50.0 miles | -
KRPD Dock | Kaskaskia River | 19.0 miles | X
Evansville Dock | Kaskaskia River | 36.4 miles | -
 | Dimension | Restriction
Length | 80’-0” | River Barge Size
Width | 50’-0” | River Barge Size
Height | 29’-6” | River Bridge Head Clearance

## Slide 34: Transportation Study

## Slide 35
Transportation Study

## Slide 36
Transportation Study

## Slide 37
An in-depth examination of the ISBL section to identify and evaluate any process or equipment risks.
  0 recommendations address “A” - Critical risk items
  0 recommendations address “B” - Serious risk items
  13 recommendations address “C” - Moderate risk items
  0 recommendations address “D” - Minor risk items
  0 recommendations address “E” - Negligible risk items
  5 recommendations address “O” - Operating issue items
Hazard and Operability (HAZOP) Review

## Slide 38: Constructability Review
Kiewit

## Slide 39
Systematic process that provides a framework for improving the project’s buildability by identifying obstacles during the pre-construction phase to reduce and prevent errors, delays, and cost overruns.
Evaluated and identified construction access, lay-down areas, lift plans, and sequencing of construction work
Constructability Review

## Slide 40
Constructability Review
Mirrored arrangement limits movement of heavy lift crane
Modules dressed and stacked directly north of plot

## Slide 41
Constructability Review – Project Schedule

## Slide 42: Carbon Capture Location
Source: Google Earth

## Slide 43: Carbon Capture Facility

## Slide 44: ISBL Detailed Engineering
Break from slideshow to review:
  Block Flow Diagram (BFD)
  ISBL Plot Plan
  Process Flow Diagram (PFD)

## Slide 45: OSBL Detailed Engineering
Break to review 3D model

## Slide 46: Review of Overall Plant Performance
Output
  8,462,000 ston annually of CO2
  95% Capture
Power Consumption: ~85.5MW
Notes: MHI load list

## Slide 47: Results and Closing Discussions
Project not currently economic without additional enhancements to federal tax credits
PSGC Owners may consider a partnership with a third-party developer/owner
Third-party developer would need to secure funding and necessary permits

## Slide 48: Acknowledgements
Name | Organization
Andrew Jones, Carl Laird | National Energy Technology Laboratory / US Department of Energy
Don Gaston, Javier Arzola, Rich Meyer | Prairie State Generating Company
Kevin O’Brien, Yongqi Lu, Vinod Patel, Stephanie Brownstein, Jason (Zhenxing) Zhang, Jason Dietsch | Prairie Research Institute / University of Illinois Urbana-Champaign
Tim Thomas, Tiffany Wu, Cole Maas | MHIA
Keisuke Iwakura, Shintaro Kiuchi | MHIENG
Matt Thomas, Alan Donovan, Bob Slettehaugh, Bryan Lofgreen | Kiewit Engineering Group
Paula Guletsky, Anthony Baker | Sargent & Lundy
This project is supported by the U.S. Department of Energy / National Energy Technology Laboratory (DOE/NETL) through Cooperative Agreement No. DE-FE0031841